## Sheet1
| Pagal ESO nuo 2023-05-19 | Huawei keitiklio nustatymai
| A0 <9.999 kW | Nustatymų meniu keitiklyje | Parametras | Rekomenduojama Vertė | Komentaras
Rekomenduojamas pirminis tinklo parametrų rinkinys | EN 50549-PL
Per aukšta įtampa 1 U> | U = 1,11 s.v. (255,3 V); | Protection Parameters | Level-1 OV protection threshold (V): | 255.3
| t = 600 s | Protection Parameters | Level-1 OV protection time (ms): | 600000
|  | Protection Parameters | 10 minute OV protection threshold (V) | 275* | *OV1 yra prioritetas - 10 min avg rekomenduojama išjungti, todėl nustatymo vertės ženkliai padidintos
|  | Protection Parameters | 10 minute OV protection time (ms): | 600000*
Per aukšta įtampa 2 U>> | U = 1,15 s.v. (264,5 V); | Protection Parameters | Level-2 OV protection threshold (V): | 264.5
| t = 0,2 s | Protection Parameters | Level-2 OV protection time (ms): | 200
Per žema įtampa 1 U< | U = 0,85 s.v. (195,5 V); | Protection Parameters | Level-1 UV protection threshold (V): | 195.5
| t = 600 s | Protection Parameters | Level-1 UV protection time (ms): | 600000
Per žema įtampa 2 U<< | U = 0,05 s.v. (11,5 V); | Protection Parameters | Level-2 UV protection threshold (V): | 11.5
| t = 0,25 s | Protection Parameters | Level-2 UV protection time (ms): | 250
Automatinis prisijungimas po įtampos ir dažnio atsistatymo |  | Grid Parameter | Automatic startup upon grid recovery: | Enable
| 0,9 – 1,1 s.v. (207 V – 253 V) | Grid Parameter | Grid reconnection voltage lower limit (V): | 207
|  | Grid Parameter | Voltage lower limit of on-grid startup (V): | 207
|  | Grid Parameter | Grid reconnection voltage upper limit (V): | 253
| 49 Hz – 50,1 Hz | Grid Parameter | Voltage upper limit of on-grid startup (V): | 253
|  | Grid Parameter | Grid reconnection frequency lower limit (Hz): | 49
|  | Grid Parameter | Frequency lower limit of on-grid startup (Hz): | 49
|  | Grid Parameter | Grid reconnection frequency upper limit (Hz): | 50.1
|  | Grid Parameter | Frequency upper limit of on-grid startup (Hz): | 50.1
| t (suveikimo) = 60 s | Grid Parameter | On-grid recovery time (s): | 60
| ΔP/Pmax ≤ 10 %/min | Grid Parameter | Soft start time after grid failure (s): | 600
|  | Grid Parameter | Quick startup for short-time grid disconnection: | Disable
Per aukštas dažnis 1 f> | [50,2-50,5 Hz]* | Protection Parameters | Level-1 OF protection threshold (Hz): | 50,2 - 50,5 | *Vertė turi būti iš intervalo 50.2 -50.5 Hz, atsitiktine tvarka.
|  | Protection Parameters | Level-1 OF protection time (ms): | 51
Per aukštas dažnis 2 f>> |  | Protection Parameters | Level-2 OF protection threshold (Hz): | 51.5** | **Nereikia keisti
|  | Protection Parameters | Level-2 OF protection time (ms): | 50
Per žemas dažnis 1 f< | 47,5 Hz ≤ f ≤ 49 Hz, | Protection Parameters | Level-1 UF protection threshold (Hz): | 49
| t ≥ 1800 s | Protection Parameters | Level-1 UF protection time (ms): | 1800000
Per žemas dažnis 2 f<< | f ≤ 47,49 Hz | Protection Parameters | Level-2 UF protection threshold (Hz): | 47.49
| t = 0,2 s | Protection Parameters | Level-2 UF protection time (ms): | 200
|  | Protection Parameters | Level-3 UF protection threshold (Hz): | 40
|  | Protection Parameters | Level-3 UF protection time (ms): | 100
Apsauga nuo dažnio kitimo spartos ROCOF [81R] | Dažnio kitimo ROCOF vertė ne mažesnė nei ± 2,5 Hz/s (t.y. lygi arba didesnė skaitinei vertei/moduliui 2,5), delsa ne mažesnė nei (t.y. lygi arba didesnė) 80 ms | Protection Parameters | Frequency change rate protection: | Enable
|  | Protection Parameters | Frequency change rate protection threshold (Hz/s): | 2.5
|  | Protection Parameters | Frequency change rate protection time (s): | 0.2
Didžiausias galios mažėjimas mažėjant dažniui | f (slenksčio) = 49 Hz | Inverter does not decrease power, if needed cut from test report can be provided
ΔP/ Pmax = 2 % per 1 Hz
Q (U) reaktyvios galios funkcija | Aktyvuota: Taip | Power Adjustment | Reactive power curve adjustment: | Q-U characteristic curve
|  | Power Adjustment | Number of Q-U characteristic curve points: | 4
| Taškas A: 209,3 V; (0,91*Un) | Power Adjustment | U/Un value of 1st Q-U curve point (%): | 91
| cosφ = 0,9 (sinφ = 0,436 Var/VA) | Power Adjustment | Q/S value of 1st Q-U curve point: | 0.436
| Taškas B: 218,5 V; (0,95*Un) | Power Adjustment | U/Un value of 2nd Q-U curve point (%): | 95
| cosφ = 1 (sinφ = 0 Var/VA) | Power Adjustment | Q/S value of 2nd Q-U curve point: | 0
| Taškas C: 242 V; (1,05*Un) | Power Adjustment | U/Un value of 3rd Q-U curve point (%): | 105
| cosφ = 1 (sinφ = 0 Var/VA) | Power Adjustment | Q/S value of 3rd Q-U curve point: | 0
| Taškas D: 250,7 V; (1,09*Un) | Power Adjustment | U/Un value of 4th Q-U curve point (%): | 109
| cosφ = - 0,9 (sinφ = -0,436 Var/VA) | Power Adjustment | Q/S value of 4th Q-U curve point: | -0.436
Įtampos ir reaktyvios galios reguliatorių laiko pastoviosios nustatymas | Nustatomas vienu iš šių būdų: Inercinė grandis (pirmos eilės filtras, angl. first order filter) nustatoma – 15 s, draudžiama < 10 s ir > 20s; Integruojanti grandis nustatoma – 30 s, draudžiama < 10 s ir >50 s; Inercinė-integruojanti grandis: nustatoma inercinė grandis – 15 s, draudžiama < 10 s ir > 20 s; nustatoma integruojanti grandis – 30 s, draudžiama < 10 s ir >50 s | Power Adjustment | Reactive power adjustment time (s): | 10 | Numatytoji reikšmė yra 10 s. EN 50549-PL nustatymuose negalima keisti.
HVRT/ | Disabled | Feature Parameter | HVRT: | Disabled
LVRT | Disabled | Feature Parameter | LVRT: | Disabled